## Revisions
Revision 1 | 2020-06-01 | VHHSBA initial release

## Table 1 Design conditions
Design Parameters – Reference table 1
Function of Space | Pressure Relationship to Adjacent Areas (n) | Minimum Outdoor ach | Minimum Total ach | All Room air Exhausted Directly to Outdoors | Air Recirculated by Means of Room Units (a) | Design Relative Humidity (k, aa)) % | Design Temperature (l) | Internal Noise from engineering services RC (ac) | Air Filtration Grade Primary / Secondry / Final | Main purpose of A/C System (ab)
SURGERY AND CRITICAL CARE
Critical and intensive care | neutral | 3 | 6 | no restriction | No | 30-60 | 21-24 | 35 | G4/F8/H13(z) | Air Conditioning
Delivery room ; Caesarean (m), (o) | Positive | 5 | 20 | no restriction | No | 30-60 | 20-24 | 40 | G4/F8/- | Air Conditioning
Emergency Department Decontamination | Negative | 3 | 12 | Yes | No | un-controlled | un-controlled | 40 | G4/F8/- | Containment
Emergency Department Exam / Treatment Room (p) | neutral | 2 | 6 | no restriction | No | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Emergency Department Public Waiting Area | Negative | 3 | 12 | Yes (q) | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Infection Control
General Clinical | neutral | 2 | 6 | no restriction | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Laser Eye Room | Positive | 3 | 15 | no restriction | No | 30-60 | 21-24 | 35 | G4/F8/- | Air Conditioning
Medical / Anaesthesia Gas Storage | Negative | no restriction | 8 | Yes | no restriction | un-controlled | un-controlled | 45 | G4/F8/- | Containment
Newborn Intensive Care | Positive | 2 | 6 | no restriction | No | 30-60 | 22-26 | 35 | G4/F8/- | Air Conditioning
Operating Room (m,o,d) | Positive | 10 | 20 | no restriction | No | 30-60 | 18-24 | 40 (c) | G4/F8/H14 | Infection Control
Cardiac OR (m,o,d) | Positive | 10 | 20 | no restriction | No | 40-60 | 16-24 | 40 (c) | G4/F8/H14 | Infection Control
Operating Room Burns / Plastics (m,o,d) | Positive | 10 | 20 | no restriction | No | 50-90 | 20-28 | 40 (c) | G4/F8/H14 | Infection Control
Hybrid Operating Room (m,o,d) | Positive | 10 | 20 | no restriction | No | 40-60 | 20-24 | 40 | G4/F8/H14 | Infection Control
Operating / surgical Cystoscopic Rooms (m,o,d) | Positive | 10 | 20 | no restriction | No | 30-60 | 20-24 | 40 | G4/F8/H14 | Infection Control
Peri-operative circulation space / corridor | neutral | 2 | 6 | no restriction | No | 30-60 | 22-26 | 40 | G4/F8/- | Air Conditioning
Cardiac Catheterisation laboratory (m,o,d) | Positive | 3 | 15 | no restriction | No | 40-60 | 20-24 | 40 | G4/F8/H14 | Infection Control
Procedure Room (m,o, d) | Positive | 4 | 15 | no restriction | No | 30-60 | 21-24 | 40 | G4/F8/H14 | Infection Control
Radiology Waiting Rooms | Negative | 3 | 12 | Yes (q), (u) | no restriction | 30-60 | 21-21 | 40 | G4/F8/- | Infection Control
Recovery Room | neutral | 2 | 6 | no restriction | No | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Substerile Service Area | neutral | 2 | 6 | no restriction | No | un-controlled | un-controlled | 50 | G4/F8/- | Air Conditioning
Rescus / Trauma Room / Crisis Hubs | Positive | 4 | 15 | no restriction | No | 30-60 | 16-24 | 40 | G4/F8/- | Air Conditioning
Treatment Room (p) | neutral | 2 | 6 | no restriction | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Triage | Negative | 3 | 12 | Yes(q) | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Wound Intensive Care, Burn Unit | neutral | 2 | 6 | no restriction | No | 40-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
INPATIENT NURSING
Classs N Anteroom ( s,r) | (e) | no restriction | 10 | Yes | No | un-controlled | un-controlled | 40 | G4/F8/- | Infection Control
Class N - Isolation Room( s,r) | Negative | 100% | 12 | Yes | No | un-controlled | 21-24 | 40 | G4/F8/- | Infection Control
Class P Anteroom (r) | (e) | no restriction | 10 | no restriction | No | un-controlled | un-controlled | 40 | G4/F8/H14 | Infection Control
Class P - Protective Environment Room (r) | Positive | 100% | 12 | no restriction | No | un-controlled | 21-26 | 40 | G4/F8/H14 | Infection Control
Classs Q Anteroom ( s,r) | (e) | no restriction | 10 | Yes | No | un-controlled | un-controlled | 40 | G4/F8/H14 | Infection Control
Class Q - Isolation Room( s,r) | Negative | 100% | 12 | Yes | No | un-controlled | 21-24 | 40 | G4/F8/H14 | Infection Control
Class P+N Combination Anteroom | (e) | 100% | 10 | Yes | No | un-controlled | un-controlled | 40 | G4/F8/H14 | Infection Control
Class P+N Patient's Room | (e) | 100% | 12 | Yes | No | un-controlled | 21-24 | 40 | G4/F8/H14 | Infection Control
Class P+N Ensuite | (e) | no restriction | 10 | no restriction | No | un-controlled | un-controlled | 40 | G4/F8/- | Air Conditioning
Continued Care Nursery | neutral | 2 | 6 | no restriction | No | un-controlled | 22-26 | 35 | G4/F8/- | Air Conditioning
Labour / Delivery / Recovery / Postpartum (LDRP) | neutral | 2 | 6 | no restriction | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Newborn Nursery Suite | neutral | 2 | 6 | no restriction | No | un-controlled | 22-26 | 35 | G4/F8/- | Air Conditioning
Tea Room / Beveridge Bay | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 21-24 | 40 | G4/F8/- | Air Conditioning
Patient Corridor | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 20-26 | 40 | G4/F8/- | Air Conditioning
Immuno-compromised Patient areas | Positive | 2 | 6 | no restriction | No | un-controlled | 20-26 | 35 | G4/F8/H14 | Infection Control
Patient Room | neutral | 2 | 6 (w) | no restriction | No | un-controlled | 21-24 | 30 | G4/F8/- | Air Conditioning
En-suite | Negative | no restriction | 10 | no restriction | No | un-controlled | un-controlled | 45 | G4/F8/- | Air Conditioning
Toilet Room | Negative | no restriction | 10 | Yes | No | un-controlled | un-controlled | 45 | G4/F8/- | Air Conditioning
NURSING FACILITY
Bathing Room | Negative | no restriction | 10 | Yes | No | un-controlled | 21-24 | 40 | G4/F7/- | Air Conditioning
Occupational Therapy | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 21-24 | 35 | G4/F7/- | Air Conditioning
Physical Therapy | Negative | 2 | 6 | no restriction | no restriction | un-controlled | 21-24 | 35 | G4/F7/- | Air Conditioning
Community Room / Activity / Dining | neutral | 4 | 8 | no restriction | no restriction | un-controlled | 21-24 | 40 | G4/F7/- | Air Conditioning
Resident Room | neutral | 2 | 2 | no restriction | no restriction | un-controlled | 21-24 | 30 | G4/F7/- | Air Conditioning
Resident Unit Corridor | neutral | no restriction | 4 | no restriction | no restriction | un-controlled | un-controlled | 40 | G4/F7/- | Air Conditioning
RADIOLOGY
Darkroom | Negative | 3 | 10 | Yes | No | un-controlled | un-controlled | 40 | G4/F8/- | Air Conditioning
X-ray (Diagnostic and Treatment) | neutral | 2 | 6 | no restriction | no restriction | 30-60 | 22-26 | 40 | G4/F8/- | Air Conditioning
X-ray (Surgical / Critical Care and Catherisation) | Positive | 3 | 15 | no restriction | No | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Magnetic Resonance Imaging (o, i) | neutral | 2 | 6 | no restriction | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
DIAGNOSTIC AND TREATMENT
Autopsy Room | Negative | 3 | 12 | Yes | No | un-controlled | 20-24 | 40 | G4/F8/- | Containment
Bronchoscopy, Sputum Collection and Pentamidine Administration | Negative | 3 | 12 | Yes | No | un-controlled | 20-23 | 40 | G4/F8/- | Infection Control
Dialysis Treatment Area | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 22-26 | 35 | G4/F8/- | Air Conditioning
Chemotherapy Treatment Area | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 22-26 | 35 | G4/F8/- | Air Conditioning
Dialyser Reprocessing Room | Negative | no restriction | 10 | Yes | No | un-controlled | un-controlled | 40 | G4/F8/- | Air Conditioning
Endoscope Cleaning | Negative | 3 | 10 | Yes | No | un-controlled | un-controlled | 40 | G4/F8/- | Air Conditioning
Gastrointestinal Endoscopy Procedure Room (v) | neutral | 2 | 6 | no restriction | No | 30-60 | 20-23 | 40 | G4/F8/- | Air Conditioning
General Examination Room | neutral | 2 | 6* | no restriction | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Hydrotherapy | Negative | 2 | 6 | no restriction | no restriction | un-controlled | 22-27 | 40 | G4/F8/- | Air Conditioning
Laboratory Work Area, Bacteriology (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Biochemistry (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Cytology (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, General (g), (t) | Negative | 2 | 6 | no restriction | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Glasswashing (g) | Negative | 3 | 10 | Yes | no restriction | 30-60 | un-controlled | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Histology (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Media Transfer (g), (t) | Positive | 2 | 4 | no restriction | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Microbiology (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Nuclear Medicine (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Pathology (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory Work Area, Serology (g), (t) | Negative | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Laboratory work Area, Sterilisating (g) | Negative | 3 | 10 | Yes | no restriction | 30-60 | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning (ad)
Medication Room | neutral | 2 | 4 | no restriction | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
MRI | neutral | 2 | 6 | Yes | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Non refrigerated Body-holding Room (h) | Negative | no restriction | 10 | Yes | No | un-controlled | 21-24 | 40 | G4/F8/- | Air Conditioning
Nuclear Medicine Hot Lab | Negative | no restriction | 6 | Yes | No | un-controlled | 21-24 | 40 (f) | G4/F8/- (y) | Air Conditioning
Nuclear Medicine Treatment Room | Negative | 2 | 6 | Yes | no restriction | un-controlled | 21-24 | 40 | G4/F8/- | Air Conditioning
Pharmacy (b) | Positive | 2 | 6 | no restriction | No | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
Physical Therapy | Negative | 2 | 6 | no restriction | no restriction | un-controlled | 22-27 | 40 | G4/F8/- | Air Conditioning
Special Examination Room (x) | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 21-24 | 40 | G4/F8/- | Air Conditioning
Treatment Room | neutral | 2 | 6 | no restriction | no restriction | 30-60 | 21-24 | 40 | G4/F8/- | Air Conditioning
STERILISATION
Steriliser Equipment Room | Negative | no restriction | 10 | Yes | No | un-controlled | un-controlled | n/a |  | Air Conditioning
STERILE PROCESSING DEPARTMENT
Clean Workroom | Positive | 2 | 6 | no restriction | No | un-controlled | 20-23 | 40 | G4/F8/H14 | Infection Control
Decontamination Room | Negative | 2 | 6 | Yes | No | un-controlled | 16-23 | 40 | G4/F8/- | Infection Control
Sterile Storage Room | Positive | 2 | 4 | N | no restriction | Min 30-Max 70 | 21-24 | n/a | G4/F8/H14 | Infection Control
SERVICES
Bathroom | Negative | no restriction | 10 | Yes | No | un-controlled | 22-26 | 45 | G4/F8/- | Air Conditioning
Clean Linen Storage | Positive | no restriction | 2 | no restriction | no restriction | un-controlled | 22-26 | 50 | G4/F8/- | Air Conditioning
Dietary Storage | neutral | no restriction | 2 | no restriction | No | un-controlled | 22-26 | 50 | G4/F8/- | Air Conditioning
Production and Re-heat Kitchens (j) | neutral | 3 | 10 | no restriction | No | un-controlled | 22-26 | 45 | G4/F8/- | Air Conditioning
Cleaners Cupboard | Negative | no restriction | 10 | Yes | No | un-controlled | un-controlled | 50 |  | Air Conditioning
Laundry, General | Negative | 3 | 10 | Yes | No | un-controlled | un-controlled | 50 | G4/F8/- | Air Conditioning
Soiled Linen Sorting and Storage | Negative | no restriction | 10 | Yes | No | un-controlled | un-controlled | 50 |  | Air Conditioning
Dirty Utility | Negative | no restriction | 10 | Yes | No | un-controlled | un-controlled | 50 |  | Air Conditioning
SUPPORT SPACE
Clean Workroom or Clean Holding | Positive | 2 | 6 | no restriction | no restriction | un-controlled | un-controlled | 40 | G4/F8/- | Air Conditioning
Hazardous Material Storage | Negative | 3 | 10 | Yes | No | un-controlled | un-controlled | n/a | G4/F8/- | Air Conditioning
Soiled Workroom or Soiled Holding | Negative | 3 | 10 | Yes | No | un-controlled | un-controlled | n/a |  | Air Conditioning
Small Meeting Room | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 21-24 | 40 | G4/F8/- | Air Conditioning
Large Meeting Room | neutral | 2 | 6 | no restriction | no restriction | un-controlled | 21-24 | 40 | G4/F8/- | Air Conditioning
Private office | neutral | 2 | 6 | no restriction | no | un-controlled | 21-24 | 40 | G4/F7/- | Air Conditioning
Atrium (j) | neutral | no restriction | no restriction | no restriction | no restriction | un-controlled | 18-26 | 45 | G4/F7/- | Air Conditioning
Footnotes
a) Except where indicated by a “No” in this column, in ceiling or wall mounted recirculating room units (with heating or cooling coils) are acceptable for providing that portion of the minimum total air changes per hour. Because of the cleaning difficulty and potential for buildup of contamination, recirculating room units shall not be used in areas marked “No.” Recirculating devices with high-efficiency particulate air (H14) filters shall be permitted in existing facilities as interim, supplemental environmental controls to meet requirements for the control of airborne infectious agents. The design of either portable or fixed systems should prevent stagnation and short circuiting of airflow. The design of such systems shall also allow for easy access for scheduled preventative maintenance and cleaning.
b) Pharmacy compounding areas may have additional air change, differential pressure, and filtering requirements beyond the minimum of this table, depending on the type of pharmacy, and the regulatory requirements the associated level of risk of the work, and the equipment used in the spaces. Refer to the appropriate Australian Standard or specialist user advice.
c) NC 55 in rooms with UCV hoods
d) Pressure relationships should be maintained when the room is unoccupied.
e)See Isolation Rooms in Volume 4 and its subsections for pressure relationship requirements.
f) NC 60 within 1m of fume cupboards
g) Higher ventilation rates above the total ach listed shall be used when dictated by the laboratory requirements and the hazard level of the potential contaminants in each laboratory work area.
h) A non refrigerated body-holding room is applicable only to facilities that do not perform autopsies on-site and use the space for short periods while waiting for the body to be transferred
i) all materials with the faraday cage shall be non-ferrous or MRI safe.
j) Minimum total air changes per hour (ach) shall be in accordance with AS1668
k) The RH ranges listed are a controlled minimum and/or maximum allowable at any point within the user controlled temperature range required for that space. Systems shall be capable of maintaining the rooms within the range during normal operation. Lower or higher humidity shall be permitted when patients’ comfort and/or medical conditions / equipment require those conditions, as a specific brief requirement. unless indicated by Min or MAX in the table. Rooms or areas that have a nominated humidity range are deemed "critical"areas, and coils will be selected for an external ambient conditoin of 26db/ 24wb.
l) The temperature ranges listed are a controlled minimum and/or maximum allowable at any point within the design temperature range required for that space. Systems shall be capable of maintaining the rooms within the range during normal operation. Lower or higher temperature shall be permitted when patients’ comfort and/or medical conditions / equipment require those conditions, as a specific brief requirement. Operating Rooms, Cath labs,proceedure Rooms and Trauma / Resusc rooms will be user adjustable.
m)50% return air will be from low level grilles. Where there is a risk of exposure to waste aesthetic gases and vapors and control of occupational exposure to nitrous oxide, local exhaust (anaesthetic gas scavenging) is required.
n) Where pressure-monitoring device alarms are installed, allowances shall be made to prevent nuisance alarms. Short-term excursions from required pressure relationships shall be allowed while doors are moving or temporarily open. Where pressure monitoring devices are not fitted, simple visual methods such as smoke trail, ball-in-tube, or flutterstrip shall be permitted for verification of airflow direction.
o) Specialist Equipment and/or surgical procedures may require room temperatures, ventilation rates, humidity ranges, and/or air distribution methods that exceed the minimum indicated ranges.
p) Treatment rooms used for bronchoscopy shall be treated as bronchoscopy rooms. Treatment rooms used for procedures with nitrous oxide shall contain provisions for exhausting anesthetic waste gases.
q) In a recirculating ventilation system, HEPA filters shall be permitted instead of exhausting the air from these spaces to the outdoors, provided that the return air passes through the HEPA filters before it is introduced into any other spaces. The entire minimum total air changes per hour of recirculating airflow shall pass through HEPA filters. When these areas are open to larger, nonwaiting spaces, the exhaust air volume shall be calculated based on the seating area of the waiting area.
r) Rooms with reversible airflow provisions for the purpose of switching between class P and class N functions shall not be permitted.
s) The class N room described in this guideline shall be used for isolating the airborne spread of infectious diseases, such as measles, varicella, or tuberculosis. When the class N room is not used for airborne infection isolation, the pressure relationship to adjacent areas, when measured with the door closed, shall remain unchanged, and the minimum total air change rate shall be 6 ach.
t) Room temperature ranges that exceed the minimum indicated range shall be permitted if required by the laboratory brief or laboratory equipment.
u) The requirement that all room air is exhausted directly to outdoors applies only to radiology waiting rooms intended to hold patients who are waiting for chest x-rays for diagnosis of respiratory disease.
v) If the planned space is designated in the organization’s operational plan to be used for both bronchoscopy and gastrointestinal endoscopy, the design parameters for “bronchoscopy, sputum collection, and pentamidine administration” shall be used.
w) For single-bed patient rooms using displacement diffusers, a minimum of six total ach shall be provided and calculated based on the volume from finished floor to 1.83 m above the floor.
x) Examination rooms for use by patients with undiagnosed gastrointestinal symptoms, undiagnosed respiratory symptoms, or undiagnosed skin symptoms
y) Filtration requirements may alter due to specialist equipment or proceedures.
z) HEPA filtration will be located in the main air handling plant
aa) In areas listed as "uncontrolled" humidity will be managed by the natural coil process, humidity levels outside the range of 30% to 60% may be experienced for parts of the year depending on the external conditions.
ab) National Construction Code of Australia "For the purposes of Section J. Air conditioning means a service that actively cools or heats air within a space, but does not include a service that directly maintains specialised conditions for equipment or processes, where this is the main purpose of the service". The main purose of the services are identified in the table as Infection Control or Containment are part of critical Heathcare processes. These systems will incorporate energy efficiency measures in accordance with NCC part J only where practical and where the measures do not interfere with the main purpose of the air conditioning system.
ac) RC curves are provided for noise from engineering services only, in the event the space under assessment are affected by other noise sources (i.e. external noise impacts, etc.) further considerations should be made by the assessing engineer to ensure adequate allowances are made to ensure the overall cumulative noise level inside the space complies with the A-Weighted number of the RC Curve.
ad) The primary purpose of the air conditioning system in PC3 or PC4 laboratories is Containment, and the systems will be designed accordingly

## Table 2 Acoustics
Design Parameters – Reference Table 2 - Acoustics
Function of Space | Internal Noise from engineering services RC (a) | Reverberation Time Objective (Seconds) | Design Vocal Effort within the Source Room (d) | Speech Privacy Level to be Achieved in the Adjoining Space (d)
SURGERY AND CRITICAL CARE
Critical and intensive care | 35 | <0.6 | Typical | Sensitive
Delivery room ; Caesarean (m), (o) | 40 | 0.4-0.6 | High | Medium Sensitive
Emergency Department Decontamination | 40 | <0.7 | Low | Not Sensitive
Emergency Department Exam / Treatment Room (p) | 40 | 0.4-0.7 | Typical | Medium Sensitive
Emergency Department Public Waiting Area | 40 | 0.4-0.6 | Typical | Medium Sensitive
General Clinical | 40 | 0.4-0.6 | Typical | Sensitive
Laser Eye Room | 35 | 0.4-0.6 | Typical | Sensitive
Medical / Anaesthesia Gas Storage | 45 | N/A | Low | Not Sensitive
Newborn Intensive Care | 35 | 0.4-0.7 | High | Sensitive
Operating Room (m,o,d) | 40 (c) | (See note b and c) | Typical | Medium Sensitive
Cardiac OR (m,o,d) | 40 (c) | (See note b and c) | Typical | Medium Sensitive
Operating Room Burns / Plastics (m,o,d) | 40 (c) | (See note b and c) | Typical | Medium Sensitive
Hybrid Operating Room (m,o,d) | 40 | (See note b and c) | Typical | Medium Sensitive
Operating / surgical Cystoscopic Rooms (m,o,d) | 40 | (See note b and c) | Typical | Medium Sensitive
Peri-operative circulation space / corridor | 40 | 0.4-0.6 | Low | Not Sensitive
Cardiac Catheterisation laboratory (m,o,d) | 40 | 0.4-0.7 | Typical | Sensitive
Procedure Room (m,o, d) | 40 | 0.4-0.7 | Typical | Sensitive
Radiology Waiting Rooms | 40 | 0.4-0.6 | Typical | Medium Sensitive
Recovery Room | 40 | 0.4-0.6 (See note b) | Typical | Sensitive
Substerile Service Area | 50 |  | Low | Not Sensitive
Rescus / Trauma Room | 40 | 0.4-0.7 | High | Medium Sensitive
Treatment Room (p) | 40 | 0.4-0.7 | Typical | Medium Sensitive
Triage | 40 | 0.4-0.7 | Typical | Sensitive
Wound Intensive Care, Burn Unit | 40 | <0.6 | Typical | Medium Sensitive
INPATIENT NURSING
Class N Anteroom ( s,r) | 40 | 0.4-0.6 | Typical | Not Sensitive
Class N - Isolation Room( s,r) | 40 | 0.4-0.7 | Typical | Medium Sensitive
Class P Anteroom (r) | 40 | 0.4-0.6 | Typical | Medium Sensitive
Class P - Protective Environment Room (r) | 40 | 0.4-0.7 | Typical | Medium Sensitive
Classs Q Anteroom ( s,r) | 40 | 0.4-0.6 | Typical | Not Sensitive
Class Q - Isolation Room( s,r) | 40 | 0.4-0.7 | Typical | Medium Sensitive
Class P+N Combination Anteroom | 40 | 0.4-0.6 | Typical | Not Sensitive
Class P+N Patient's Room | 40 | 0.4-0.7 | Typical | Medium Sensitive
Class P+N Ensuite | 40 | n/a | Typical | Not Sensitive
Continued Care Nursery | 35 | 0.4-1.0 | Typical | Medium Sensitive
Labour / Delivery / Recovery / Postpartum (LDRP) | 40 | 0.4-0.6 (See note c) | High | Sensitive
Newborn Nursery Suite | 35 | 0.4-1.0 | Typical | Sensitive
Tea Room / Beveridge Bay | 40 | 0.4-0.6 | Low | Not Sensitive
Patient Corridor | 40 | 0.4-0.6 | Typical | Not Sensitive
Immuno-compromised Patient areas | 35 | 0.4-0.6 | Typical | Medium Sensitive
Patient Room | 30 | 0.4-0.7 | Typical | Medium Sensitive
En-suite | 45 | n/a | Typical | Not Sensitive
Toilet Room | 45 | n/a | Typical | Not Sensitive
NURSING FACILITY
Bathing Room | 40 | 0.4-0.7 | Typical | Medium Sensitive
Obupational Therapy | 35 | 0.4-0.6 | Typical | Sensitive
Physical Therapy | 35 | 0.4-0.6 | Typical | Sensitive
Community Room / Activity / Dining | 40 | (see note b) | Typical | Medium Sensitive
Resident Room | 30 | 0.4-0.7 | Typical | Medium Sensitive
Resident Unit Corridor | 40 | 0.4-0.6 | Typical | Not Sensitive
RADIOLOGY
Darkroom | 40 | (see note b) | Typical | Medium Sensitive
X-ray (Diagnostic and Treatment) | 40 | (see note b) | Typical | Medium Sensitive
X-ray (Surgical / Critical Care and Catherisation) | 40 | (see note b) | Typical | Medium Sensitive
Magnetic Resonance Imaging (o, i) | 40 | (see note b) | Typical | Medium Sensitive
DIAGNOSTIC AND TREATMENT
Autopsy Room | 40 | 0.4-0.7 | Typical | Sensitive
Bronchoscopy, Sputum Collection and Pentamidine Administration | 40 | 0.4-0.6 | High | Medium Sensitive
Dialysis Treatment Area | 35 | 0.4-0.7 | Typical | Sensitive
Chemotherapy Treatment Area | 35 | 0.4-0.7 | Typical | Sensitive
Dialyser Reprocessing Room | 40 | 0.4-0.7 | Typical | Medium Sensitive
Endoscope Cleaning | 40 | 04.-0.7 | Low | Not Sensitive
Gastrointestinal Endoscopy Procedure Room (v) | 40 | 0.4-0.7 | Typical | Sensitive
General Examination Room | 40 | 0.4-0.6 | Typical | Sensitive
Hydrotherapy | 40 | 0.4-0.7 | High | Not Sensitive
Laboratory Work Area, Bacteriology (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Biochemistry (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Cytology (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, General (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Glasswashing (g) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Histology (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Media Transfer (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Microbiology (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Nuclear Medicine (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Pathology (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory Work Area, Serology (g), (t) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Laboratory work Area, Sterilisating (g) | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Medication Room | 40 | 0.4-0.7 | Typical | Medium Sensitive
MRI | 40 | (see note b) | Typical | Sensitive
Non refrigerated Body-holding Room (h) | 40 | N/A | Low | Not Sensitive
Nuclear Medicine Hot Lab | 40 (f) | 0.4-0.7 | Typical | Medium Sensitive
Nuclear Medicine Treatment Room | 40 | 0.4-0.7 | Typical | Sensitive
Pharmacy (b) | 40 | 0.4-0.6 | Typical | Medium Sensitive
Physical Therapy | 40 | 0.4-0.7 | High | Medium Sensitive
Special Examination Room (x) | 40 | 0.4-0.6 | High | Sensitive
Treatment Room | 40 | 0.4-0.7 | Typical | Sensitive
STERILISATION
Steriliser Equipment Room | n/a | n/a | n/a | n/a
STERILE PROCESSING DEPARTMENT
Clean Workroom | 40 | 0.4-0.7 | Typical | Not Sensitive
Decontamination Room | 40 | 0.4-0.7 | Typical | Not Sensitive
Sterile Storage Room | n/a | n/a | Low | Not Sensitive
SERVICES
Bathroom | 45 | n/a | Typical | Not Sensitive
Clean Linen Storage | 50 | n/a | Low | Not Sensitive
Dietary Storage | 50 | n/a | Low | Not Sensitive
Production and Re-heat Kitchens (j) | 45 | <0.8 (See note c) | Very High | Not Sensitive
Cleaners Cupboard | 50 | n/a | Low | Not Sensitive
Laundry, General | 50 | n/a | Low | Not Sensitive
Soiled Linen Sorting and Storage | 50 | n/a | Low | Not Sensitive
Dirty Utility | 50 | n/a | High | Not Sensitive
SUPPORT SPACE
Clean Workroom or Clean Holding | 40 | 0.4-0.7 | Typical | Not Sensitive
Hazardous Material Storage | n/a | n/a | Low | Not Sensitive
Soiled Workroom or Soiled Holding | n/a | n/a | Typical | Not Sensitive
Small Meeting Room | 40 | <0.6 | Typical | Sensitive
Large Meeting Room | 40 | 0.6-0.8 | High | Sensitive
Private office | 40 | 0.4-0.6 | Typical | Sensitive
Atrium | 45 | e) | Typical | n/a
Footnotes
a) RC curves are provided for noise from engineering services only, in the event the space under assessment are affected by other noise sources (i.e. external noise impacts, etc.) further considerations should be made by the assessing engineer to ensure adequate allowances are made to ensure the overall cumulative noise level inside the space complies with the A-Weighted number of the RC Curve.
b) Notes section of Table 1 of AS NZ 2107:2016 Acoustics - Recommended design sound levels and reverberation times for building interiors states the following; under note 1 that the reverberation time in this space should be minimised as far as practical.
c) Notes section of Table 1 of AS NZ 2107:2016 Acoustics - Recommended design sound levels and reverberation times for building interiors states the following; under note 8 states Health requirements for hygiene and infection control may prelude achieving these recommended reverberation times.
d) In the determination of acoustic privacy requirement between spaces, the formaula of " R' = D + 10 log S/A dB " shall be used, in abordance with AS ISO 140.4-2006. (D = level difference (refer to Appendix (LCI TO DETERMINE LOCATION OF Appendix)). S = is the area of the seperating element. A = is the equivalent sound absorption in the receiving room.)
e) Curve 4 in Figure A1 (Appendix A) of AZ/NZS2107:2016.