## Reference Table 3
Reference Table 3 - Required Noise Reductions for Room Adjacencies
Space Type | SURGERY AND CRITICAL CARE | Critical and intensive care | Delivery room ; Caesarean (m), (o) | Emergency Department Decontamination | Emergency Department Exam / Treatment Room (p) | Emergency Department Public Waiting Area | General Clinical | Laser Eye Room | Medical / Anaesthesia Gas Storage | Newborn Intensive Care | Operating Room (m,o,d) | Cardiac OR (m,o,d) | Operating Room Burns / Plastics (m,o,d) | Hybrid Operating Room (m,o,d) | Operating / surgical Cystoscopic Rooms (m,o,d) | Peri-operative circulation space / corridor | Cardiac Catheterisation laboratory (m,o,d) | Procedure Room (m,o, d) | Radiology Waiting Rooms | Recovery Room | Substerile Service Area | Rescus / Trauma Room | Treatment Room (p) | Triage | Wound Intensive Care, Burn Unit | INPATIENT NURSING | Class N Anteroom ( s,r) | Class N - Isolation Room( s,r) | Class P Anteroom (r) | Class P - Protective Environment Room (r) | Classs Q Anteroom ( s,r) | Class Q - Isolation Room( s,r) | Class P+N Combination Anteroom | Class P+N Patient's Room | Class P+N Ensuite | Continued Care Nursery | Labour / Delivery / Recovery / Postpartum (LDRP) | Newborn Nursery Suite | Tea Room / Beveridge Bay | Patient Corridor | Immuno-compromised Patient areas | Patient Room | En-suite | Toilet Room | NURSING FACILITY | Bathing Room | Obupational Therapy | Physical Therapy | Community Room / Activity / Dining | Resident Room | Resident Unit Corridor | RADIOLOGY | Darkroom | X-ray (Diagnostic and Treatment) | X-ray (Surgical / Critical Care and Catherisation) | Magnetic Resonance Imaging (o, i) | DIAGNOSTIC AND TREATMENT | Autopsy Room | Bronchoscopy, Sputum Collection and Pentamidine Administration | Dialysis Treatment Area | Chemotherapy Treatment Area | Dialyser Reprocessing Room | Endoscope Cleaning | Gastrointestinal Endoscopy Procedure Room (v) | General Examination Room | Hydrotherapy | Laboratory Work Area, Bacteriology (g), (t) | Laboratory Work Area, Biochemistry (g), (t) | Laboratory Work Area, Cytology (g), (t) | Laboratory Work Area, General (g), (t) | Laboratory Work Area, Glasswashing (g) | Laboratory Work Area, Histology (g), (t) | Laboratory Work Area, Media Transfer (g), (t) | Laboratory Work Area, Microbiology (g), (t) | Laboratory Work Area, Nuclear Medicine (g), (t) | Laboratory Work Area, Pathology (g), (t) | Laboratory Work Area, Serology (g), (t) | Laboratory work Area, Sterilisating (g) | Medication Room | MRI | Non refrigerated Body-holding Room (h) | Nuclear Medicine Hot Lab | Nuclear Medicine Treatment Room | Pharmacy (b) | Physical Therapy | Special Examination Room (x) | Treatment Room | STERILISATION | Steriliser Equipment Room | STERILE PROCESSING DEPARTMENT | Clean Workroom | Decontamination Room | Sterile Storage Room | SERVICES | Bathroom | Clean Linen Storage | Dietary Storage | Production and Re-heat Kitchens (j) | Cleaners Cupboard | Laundry, General | Soiled Linen Sorting and Storage | Dirty Utility | SUPPORT SPACE | Clean Workroom or Clean Holding | Hazardous Material Storage | Soiled Workroom or Soiled Holding | Small Meeting Room | Large Meeting Room | Private office
SURGERY AND CRITICAL CARE
Critical and intensive care |  | 46 | 53 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 40 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 |  | 46 | 53 | 46 | 46 | 46 | 40 | 46 | 46 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 53 | 53 | 46 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 46 | 53 | 46
Delivery room ; Caesarean (m), (o) |  | 53 | 41 | 36 | 41 | 41 | 48 | 53 | 31 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 29 | 41 | 41 | 48 | 41 |  | 36 | 41 | 41 | 41 | 36 | 41 | 36 | 41 | 36 | 46 | 48 | 53 | 36 | 36 | 46 | 51 | 35 | 35 |  | 41 | 53 | 53 | 41 | 51 | 36 |  | 41 | 41 | 41 | 41 |  | 48 | 41 | 53 | 53 | 41 | 36 | 48 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 41 | 48 | 48 |  | 29 |  | 36 | 36 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 36 | 29 | 35 | 48 | 48 | 48
Emergency Department Decontamination |  | 40 | 36 | 24 | 30 | 30 | 35 | 40 | 24 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 30 | 35 | 24 | 36 | 30 | 35 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 36 | 40 | 24 | 30 | 34 | 39 | 30 | 30 |  | 30 | 40 | 40 | 30 | 39 | 30 |  | 30 | 30 | 30 | 30 |  | 35 | 36 | 40 | 40 | 30 | 24 | 35 | 35 | 36 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 24 | 30 | 35 | 30 | 36 | 36 | 35 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 35 | 36 | 35
Emergency Department Exam / Treatment Room (p) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Emergency Department Public Waiting Area |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
General Clinical |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Laser Eye Room |  | 46 | 53 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 40 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 |  | 46 | 53 | 46 | 46 | 46 | 40 | 46 | 46 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 53 | 53 | 46 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 46 | 53 | 46
Medical / Anaesthesia Gas Storage |  | 40 | 31 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 19 | 31 | 29 | 35 | 29 |  | 25 | 29 | 29 | 29 | 25 | 29 | 25 | 29 | 25 | 34 | 35 | 40 | 24 | 25 | 34 | 39 | 25 | 25 |  | 29 | 40 | 40 | 29 | 39 | 25 |  | 29 | 29 | 29 | 29 |  | 35 | 31 | 40 | 40 | 29 | 24 | 35 | 35 | 31 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 31 | 35 | 35 |  | 19 |  | 25 | 25 | 19 |  | 25 | 19 | 19 | 37 | 19 | 19 | 19 | 31 |  | 25 | 19 | 25 | 35 | 35 | 35
Newborn Intensive Care |  | 53 | 53 | 40 | 46 | 46 | 48 | 53 | 40 | 53 | 48 | 48 | 48 | 48 | 48 | 40 | 48 | 48 | 46 | 48 | 40 | 53 | 46 | 48 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 53 | 40 | 46 | 46 | 51 | 46 | 46 |  | 46 | 53 | 53 | 46 | 51 | 46 |  | 46 | 46 | 46 | 46 |  | 48 | 53 | 53 | 53 | 46 | 40 | 48 | 48 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 48 | 40 | 46 | 48 | 46 | 53 | 53 | 48 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 48 | 53 | 48
Operating Room (m,o,d) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Cardiac OR (m,o,d) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Operating Room Burns / Plastics (m,o,d) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Hybrid Operating Room (m,o,d) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Operating / surgical Cystoscopic Rooms (m,o,d) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Peri-operative circulation space / corridor |  | 40 | 36 | 24 | 30 | 30 | 35 | 40 | 24 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 30 | 35 | 24 | 36 | 30 | 35 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 36 | 40 | 24 | 30 | 34 | 39 | 30 | 30 |  | 30 | 40 | 40 | 30 | 39 | 30 |  | 30 | 30 | 30 | 30 |  | 35 | 36 | 40 | 40 | 30 | 24 | 35 | 35 | 36 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 24 | 30 | 35 | 30 | 36 | 36 | 35 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 35 | 36 | 35
Cardiac Catheterisation laboratory (m,o,d) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Procedure Room (m,o, d) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Radiology Waiting Rooms |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Recovery Room |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Substerile Service Area |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
Rescus / Trauma Room |  | 53 | 41 | 36 | 41 | 41 | 48 | 53 | 31 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 29 | 41 | 41 | 48 | 41 |  | 36 | 41 | 41 | 41 | 36 | 41 | 36 | 41 | 36 | 46 | 48 | 53 | 36 | 36 | 46 | 51 | 35 | 35 |  | 41 | 53 | 53 | 41 | 51 | 36 |  | 41 | 41 | 41 | 41 |  | 48 | 41 | 53 | 53 | 41 | 36 | 48 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 41 | 48 | 48 |  | 29 |  | 36 | 36 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 36 | 29 | 35 | 48 | 48 | 48
Treatment Room (p) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Triage |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Wound Intensive Care, Burn Unit |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
INPATIENT NURSING
Class N Anteroom ( s,r) |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Class N - Isolation Room( s,r) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Class P Anteroom (r) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Class P - Protective Environment Room (r) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Classs Q Anteroom ( s,r) |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Class Q - Isolation Room( s,r) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Class P+N Combination Anteroom |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Class P+N Patient's Room |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Class P+N Ensuite |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Continued Care Nursery |  | 46 | 46 | 34 | 40 | 40 | 41 | 46 | 34 | 46 | 41 | 41 | 41 | 41 | 41 | 34 | 41 | 41 | 40 | 41 | 34 | 46 | 40 | 41 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 46 | 46 | 34 | 40 | 40 | 45 | 40 | 40 |  | 40 | 46 | 46 | 40 | 45 | 40 |  | 40 | 40 | 40 | 40 |  | 41 | 46 | 46 | 46 | 40 | 34 | 41 | 41 | 46 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 34 | 40 | 41 | 40 | 46 | 46 | 41 |  | 34 |  | 40 | 40 | 34 |  | 40 | 34 | 34 | 53 | 34 | 34 | 34 | 46 |  | 40 | 34 | 40 | 41 | 46 | 41
Labour / Delivery / Recovery / Postpartum (LDRP) |  | 53 | 48 | 36 | 41 | 41 | 48 | 53 | 35 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 35 | 48 | 41 | 48 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 46 | 48 | 53 | 36 | 41 | 46 | 51 | 41 | 41 |  | 41 | 53 | 53 | 41 | 51 | 41 |  | 41 | 41 | 41 | 41 |  | 48 | 48 | 53 | 53 | 41 | 36 | 48 | 48 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 48 | 48 | 48 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 48 | 48 | 48
Newborn Nursery Suite |  | 46 | 53 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 40 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 |  | 46 | 53 | 46 | 46 | 46 | 40 | 46 | 46 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 53 | 53 | 46 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 46 | 53 | 46
Tea Room / Beveridge Bay |  | 40 | 36 | 24 | 30 | 30 | 35 | 40 | 24 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 30 | 35 | 24 | 36 | 30 | 35 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 36 | 40 | 24 | 30 | 34 | 39 | 30 | 30 |  | 30 | 40 | 40 | 30 | 39 | 30 |  | 30 | 30 | 30 | 30 |  | 35 | 36 | 40 | 40 | 30 | 24 | 35 | 35 | 36 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 24 | 30 | 35 | 30 | 36 | 36 | 35 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 35 | 36 | 35
Patient Corridor |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Immuno-compromised Patient areas |  | 46 | 46 | 34 | 40 | 40 | 41 | 46 | 34 | 46 | 41 | 41 | 41 | 41 | 41 | 34 | 41 | 41 | 40 | 41 | 34 | 46 | 40 | 41 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 46 | 46 | 34 | 40 | 40 | 45 | 40 | 40 |  | 40 | 46 | 46 | 40 | 45 | 40 |  | 40 | 40 | 40 | 40 |  | 41 | 46 | 46 | 46 | 40 | 34 | 41 | 41 | 46 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 34 | 40 | 41 | 40 | 46 | 46 | 41 |  | 34 |  | 40 | 40 | 34 |  | 40 | 34 | 34 | 53 | 34 | 34 | 34 | 46 |  | 40 | 34 | 40 | 41 | 46 | 41
Patient Room |  | 46 | 51 | 39 | 45 | 45 | 45 | 46 | 39 | 51 | 45 | 45 | 45 | 45 | 45 | 39 | 45 | 45 | 45 | 45 | 39 | 51 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 51 | 46 | 39 | 45 | 45 | 45 | 45 | 45 |  | 45 | 46 | 46 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 |  | 45 | 51 | 46 | 46 | 45 | 39 | 45 | 45 | 51 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 39 | 45 | 45 | 45 | 51 | 51 | 45 |  | 39 |  | 45 | 45 | 39 |  | 45 | 39 | 39 | 58 | 39 | 39 | 39 | 51 |  | 45 | 39 | 45 | 45 | 51 | 45
En-suite |  | 46 | 35 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 20 | 35 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 25 | 25 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 35 | 46 | 46 | 35 | 30 | 41 | 41 | 31 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 35 | 41 | 41 |  | 20 |  | 30 | 30 | 20 |  | 25 | 20 | 20 | 37 | 20 | 20 | 20 | 31 |  | 30 | 20 | 25 | 41 | 41 | 41
Toilet Room |  | 46 | 35 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 20 | 35 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 25 | 25 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 35 | 46 | 46 | 35 | 30 | 41 | 41 | 31 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 35 | 41 | 41 |  | 20 |  | 30 | 30 | 20 |  | 25 | 20 | 20 | 37 | 20 | 20 | 20 | 31 |  | 30 | 20 | 25 | 41 | 41 | 41
NURSING FACILITY
Bathing Room |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Obupational Therapy |  | 46 | 53 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 40 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 |  | 46 | 53 | 46 | 46 | 46 | 40 | 46 | 46 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 53 | 53 | 46 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 46 | 53 | 46
Physical Therapy |  | 46 | 53 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 40 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 |  | 46 | 53 | 46 | 46 | 46 | 40 | 46 | 46 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 53 | 53 | 46 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 46 | 53 | 46
Community Room / Activity / Dining |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Resident Room |  | 46 | 51 | 39 | 45 | 45 | 45 | 46 | 39 | 51 | 45 | 45 | 45 | 45 | 45 | 39 | 45 | 45 | 45 | 45 | 39 | 51 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 51 | 46 | 39 | 45 | 45 | 45 | 45 | 45 |  | 45 | 46 | 46 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 |  | 45 | 51 | 46 | 46 | 45 | 39 | 45 | 45 | 51 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 39 | 45 | 45 | 45 | 51 | 51 | 45 |  | 39 |  | 45 | 45 | 39 |  | 45 | 39 | 39 | 58 | 39 | 39 | 39 | 51 |  | 45 | 39 | 45 | 45 | 51 | 45
Resident Unit Corridor |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
RADIOLOGY
Darkroom |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
X-ray (Diagnostic and Treatment) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
X-ray (Surgical / Critical Care and Catherisation) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Magnetic Resonance Imaging (o, i) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
DIAGNOSTIC AND TREATMENT
Autopsy Room |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Bronchoscopy, Sputum Collection and Pentamidine Administration |  | 53 | 41 | 36 | 41 | 41 | 48 | 53 | 31 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 29 | 41 | 41 | 48 | 41 |  | 36 | 41 | 41 | 41 | 36 | 41 | 36 | 41 | 36 | 46 | 48 | 53 | 36 | 36 | 46 | 51 | 35 | 35 |  | 41 | 53 | 53 | 41 | 51 | 36 |  | 41 | 41 | 41 | 41 |  | 48 | 41 | 53 | 53 | 41 | 36 | 48 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 41 | 48 | 48 |  | 29 |  | 36 | 36 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 36 | 29 | 35 | 48 | 48 | 48
Dialysis Treatment Area |  | 46 | 53 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 40 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 |  | 46 | 53 | 46 | 46 | 46 | 40 | 46 | 46 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 53 | 53 | 46 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 46 | 53 | 46
Chemotherapy Treatment Area |  | 46 | 53 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 46 | 40 | 53 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 40 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 |  | 46 | 53 | 46 | 46 | 46 | 40 | 46 | 46 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 46 | 46 | 46 | 53 | 53 | 46 |  | 40 |  | 46 | 46 | 40 |  | 46 | 40 | 40 | 59 | 40 | 40 | 40 | 53 |  | 46 | 40 | 46 | 46 | 53 | 46
Dialyser Reprocessing Room |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Endoscope Cleaning |  | 40 | 36 | 24 | 30 | 30 | 35 | 40 | 24 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 30 | 35 | 24 | 36 | 30 | 35 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 36 | 40 | 24 | 30 | 34 | 39 | 30 | 30 |  | 30 | 40 | 40 | 30 | 39 | 30 |  | 30 | 30 | 30 | 30 |  | 35 | 36 | 40 | 40 | 30 | 24 | 35 | 35 | 36 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 24 | 30 | 35 | 30 | 36 | 36 | 35 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 35 | 36 | 35
Gastrointestinal Endoscopy Procedure Room (v) |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
General Examination Room |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Hydrotherapy |  | 53 | 41 | 36 | 41 | 41 | 48 | 53 | 31 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 26 | 41 | 41 | 48 | 41 |  | 36 | 41 | 41 | 41 | 36 | 41 | 36 | 41 | 36 | 46 | 48 | 53 | 36 | 36 | 46 | 51 | 31 | 31 |  | 41 | 53 | 53 | 41 | 51 | 36 |  | 41 | 41 | 41 | 41 |  | 48 | 41 | 53 | 53 | 41 | 36 | 48 | 48 | 36 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 41 | 48 | 48 |  | 26 |  | 36 | 36 | 26 |  | 31 | 26 | 26 | 42 | 26 | 26 | 26 | 36 |  | 36 | 26 | 30 | 48 | 48 | 48
Laboratory Work Area, Bacteriology (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Biochemistry (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Cytology (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, General (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Glasswashing (g) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Histology (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Media Transfer (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Microbiology (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Nuclear Medicine (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Pathology (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory Work Area, Serology (g), (t) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Laboratory work Area, Sterilisating (g) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Medication Room |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
MRI |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Non refrigerated Body-holding Room (h) |  | 40 | 36 | 24 | 30 | 30 | 35 | 40 | 24 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 30 | 35 | 24 | 36 | 30 | 35 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 36 | 40 | 24 | 30 | 34 | 39 | 30 | 30 |  | 30 | 40 | 40 | 30 | 39 | 30 |  | 30 | 30 | 30 | 30 |  | 35 | 36 | 40 | 40 | 30 | 24 | 35 | 35 | 36 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 24 | 30 | 35 | 30 | 36 | 36 | 35 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 35 | 36 | 35
Nuclear Medicine Hot Lab |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Nuclear Medicine Treatment Room |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Pharmacy (b) |  | 46 | 41 | 30 | 35 | 35 | 41 | 46 | 29 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 29 | 41 | 35 | 41 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 41 | 46 | 30 | 35 | 40 | 45 | 35 | 35 |  | 35 | 46 | 46 | 35 | 45 | 35 |  | 35 | 35 | 35 | 35 |  | 41 | 41 | 46 | 46 | 35 | 30 | 41 | 41 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 41 | 41 | 41 |  | 29 |  | 35 | 35 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 35 | 29 | 35 | 41 | 41 | 41
Physical Therapy |  | 53 | 41 | 36 | 41 | 41 | 48 | 53 | 31 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 29 | 41 | 41 | 48 | 41 |  | 36 | 41 | 41 | 41 | 36 | 41 | 36 | 41 | 36 | 46 | 48 | 53 | 36 | 36 | 46 | 51 | 35 | 35 |  | 41 | 53 | 53 | 41 | 51 | 36 |  | 41 | 41 | 41 | 41 |  | 48 | 41 | 53 | 53 | 41 | 36 | 48 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 41 | 48 | 48 |  | 29 |  | 36 | 36 | 29 |  | 35 | 29 | 29 | 48 | 29 | 29 | 29 | 41 |  | 36 | 29 | 35 | 48 | 48 | 48
Special Examination Room (x) |  | 53 | 48 | 36 | 41 | 41 | 48 | 53 | 35 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 35 | 48 | 41 | 48 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 46 | 48 | 53 | 36 | 41 | 46 | 51 | 41 | 41 |  | 41 | 53 | 53 | 41 | 51 | 41 |  | 41 | 41 | 41 | 41 |  | 48 | 48 | 53 | 53 | 41 | 36 | 48 | 48 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 48 | 48 | 48 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 48 | 48 | 48
Treatment Room |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 |  | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
STERILISATION
Steriliser Equipment Room |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
STERILE PROCESSING DEPARTMENT
Clean Workroom |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Decontamination Room |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Sterile Storage Room |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
SERVICES
Bathroom |  | 46 | 35 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 20 | 35 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 25 | 25 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 35 | 46 | 46 | 35 | 30 | 41 | 41 | 31 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 35 | 41 | 41 |  | 20 |  | 30 | 30 | 20 |  | 25 | 20 | 20 | 37 | 20 | 20 | 20 | 31 |  | 30 | 20 | 25 | 41 | 41 | 41
Clean Linen Storage |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
Dietary Storage |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
Production and Re-heat Kitchens (j) |  | 59 | 48 | 42 | 48 | 48 | 54 | 59 | 37 | 59 | 54 | 54 | 54 | 54 | 54 | 42 | 54 | 54 | 48 | 54 | 32 | 48 | 48 | 54 | 48 |  | 42 | 48 | 48 | 48 | 42 | 48 | 42 | 48 | 42 | 53 | 54 | 59 | 42 | 42 | 53 | 58 | 37 | 37 |  | 48 | 59 | 59 | 48 | 58 | 42 |  | 48 | 48 | 48 | 48 |  | 54 | 48 | 59 | 59 | 48 | 42 | 54 | 54 | 42 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 54 | 42 | 48 | 54 | 48 | 48 | 54 | 54 |  | 32 |  | 42 | 42 | 32 |  | 37 | 32 | 32 | 37 | 32 | 32 | 32 | 32 |  | 42 | 32 | 32 | 54 | 54 | 54
Cleaners Cupboard |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
Laundry, General |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
Soiled Linen Sorting and Storage |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
Dirty Utility |  | 53 | 41 | 36 | 41 | 41 | 48 | 53 | 31 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 26 | 41 | 41 | 48 | 41 |  | 36 | 41 | 41 | 41 | 36 | 41 | 36 | 41 | 36 | 46 | 48 | 53 | 36 | 36 | 46 | 51 | 31 | 31 |  | 41 | 53 | 53 | 41 | 51 | 36 |  | 41 | 41 | 41 | 41 |  | 48 | 41 | 53 | 53 | 41 | 36 | 48 | 48 | 36 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 41 | 48 | 48 |  | 26 |  | 36 | 36 | 26 |  | 31 | 26 | 26 | 32 | 26 | 26 | 26 | 26 |  | 36 | 26 | 26 | 48 | 48 | 48
SUPPORT SPACE
Clean Workroom or Clean Holding |  | 46 | 36 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 24 | 36 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 30 | 30 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 36 | 46 | 46 | 35 | 30 | 41 | 41 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 36 | 41 | 41 |  | 24 |  | 30 | 30 | 24 |  | 30 | 24 | 24 | 42 | 24 | 24 | 24 | 36 |  | 30 | 24 | 30 | 41 | 41 | 41
Hazardous Material Storage |  | 40 | 29 | 24 | 29 | 29 | 35 | 40 | 19 | 40 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 29 | 35 | 14 | 29 | 29 | 35 | 29 |  | 24 | 29 | 29 | 29 | 24 | 29 | 24 | 29 | 24 | 34 | 35 | 40 | 24 | 24 | 34 | 39 | 20 | 20 |  | 29 | 40 | 40 | 29 | 39 | 24 |  | 29 | 29 | 29 | 29 |  | 35 | 29 | 40 | 40 | 29 | 24 | 35 | 35 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 35 | 24 | 29 | 35 | 29 | 29 | 35 | 35 |  | 14 |  | 24 | 24 | 14 |  | 20 | 14 | 14 | 32 | 14 | 14 | 14 | 26 |  | 24 | 14 | 20 | 35 | 35 | 35
Soiled Workroom or Soiled Holding |  | 46 | 35 | 30 | 35 | 35 | 41 | 46 | 25 | 46 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 | 35 | 41 | 20 | 35 | 35 | 41 | 35 |  | 30 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 30 | 40 | 41 | 46 | 30 | 30 | 40 | 45 | 25 | 25 |  | 35 | 46 | 46 | 35 | 45 | 30 |  | 35 | 35 | 35 | 35 |  | 41 | 35 | 46 | 46 | 35 | 30 | 41 | 41 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 30 | 35 | 41 | 35 | 35 | 41 | 41 |  | 20 |  | 30 | 30 | 20 |  | 25 | 20 | 20 | 32 | 20 | 20 | 20 | 26 |  | 30 | 20 | 20 | 41 | 41 | 41
Small Meeting Room |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 | 0 | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41
Large Meeting Room |  | 53 | 48 | 36 | 41 | 41 | 48 | 53 | 35 | 53 | 48 | 48 | 48 | 48 | 48 | 36 | 48 | 48 | 41 | 48 | 35 | 48 | 41 | 48 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 46 | 48 | 53 | 36 | 41 | 46 | 51 | 41 | 41 |  | 41 | 53 | 53 | 41 | 51 | 41 |  | 41 | 41 | 41 | 41 |  | 48 | 48 | 53 | 53 | 41 | 36 | 48 | 48 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 36 | 41 | 48 | 41 | 48 | 48 | 48 |  | 35 | 0 | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 48 | 48 | 41
Private office |  | 46 | 48 | 35 | 41 | 41 | 41 | 46 | 35 | 48 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 41 | 35 | 48 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 48 | 46 | 35 | 41 | 41 | 45 | 41 | 41 |  | 41 | 46 | 46 | 41 | 45 | 41 |  | 41 | 41 | 41 | 41 |  | 41 | 48 | 46 | 46 | 41 | 35 | 41 | 41 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 41 | 41 | 41 | 48 | 48 | 41 |  | 35 | 0 | 41 | 41 | 35 |  | 41 | 35 | 35 | 54 | 35 | 35 | 35 | 48 |  | 41 | 35 | 41 | 41 | 48 | 41

## Pull Down version
Reference Table 3 - Pull Down
| Reference Space 1 | Cardiac Catheterisation laboratory (m,o,d)
| Reference Space 2 | Class P Anteroom (r)
| Required Noise Reductions for Room Adjacencies | 41
Critical and intensive care
Delivery room ; Caesarean (m), (o)
Emergency Department Decontamination
Emergency Department Exam / Treatment Room (p)
Emergency Department Public Waiting Area
General Clinical
Laser Eye Room
Medical / Anaesthesia Gas Storage
Newborn Intensive Care
Operating Room (m,o,d)
Cardiac OR (m,o,d)
Operating Room Burns / Plastics (m,o,d)
Hybrid Operating Room (m,o,d)
Operating / surgical Cystoscopic Rooms (m,o,d)
Peri-operative circulation space / corridor
Cardiac Catheterisation laboratory (m,o,d)
Procedure Room (m,o, d)
Radiology Waiting Rooms
Recovery Room
Substerile Service Area
Rescus / Trauma Room
Treatment Room (p)
Triage
Wound Intensive Care, Burn Unit
Class N Anteroom ( s,r)
Class N - Isolation Room( s,r)
Class P Anteroom (r)
Class P - Protective Environment Room (r)
Classs Q Anteroom ( s,r)
Class Q - Isolation Room( s,r)
Class P+N Combination Anteroom
Class P+N Patient's Room
Class P+N Ensuite
Continued Care Nursery
Labour / Delivery / Recovery / Postpartum (LDRP)
Newborn Nursery Suite
Tea Room / Beveridge Bay
Patient Corridor
Immuno-compromised Patient areas
Patient Room
En-suite
Toilet Room
Bathing Room
Obupational Therapy
Physical Therapy
Community Room / Activity / Dining
Resident Room
Resident Unit Corridor
Darkroom
X-ray (Diagnostic and Treatment)
X-ray (Surgical / Critical Care and Catherisation)
Magnetic Resonance Imaging (o, i)
Autopsy Room
Bronchoscopy, Sputum Collection and Pentamidine Administration
Dialysis Treatment Area
Chemotherapy Treatment Area
Dialyser Reprocessing Room
Endoscope Cleaning
Gastrointestinal Endoscopy Procedure Room (v)
General Examination Room
Hydrotherapy
Laboratory Work Area, Bacteriology (g), (t)
Laboratory Work Area, Biochemistry (g), (t)
Laboratory Work Area, Cytology (g), (t)
Laboratory Work Area, General (g), (t)
Laboratory Work Area, Glasswashing (g)
Laboratory Work Area, Histology (g), (t)
Laboratory Work Area, Media Transfer (g), (t)
Laboratory Work Area, Microbiology (g), (t)
Laboratory Work Area, Nuclear Medicine (g), (t)
Laboratory Work Area, Pathology (g), (t)
Laboratory Work Area, Serology (g), (t)
Laboratory work Area, Sterilisating (g)
Medication Room
MRI
Non refrigerated Body-holding Room (h)
Nuclear Medicine Hot Lab
Nuclear Medicine Treatment Room
Pharmacy (b)
Physical Therapy
Special Examination Room (x)
Treatment Room
Steriliser Equipment Room
Clean Workroom
Decontamination Room
Sterile Storage Room
Bathroom
Clean Linen Storage
Dietary Storage
Production and Re-heat Kitchens (j)
Cleaners Cupboard
Laundry, General
Soiled Linen Sorting and Storage
Dirty Utility
Clean Workroom or Clean Holding
Hazardous Material Storage
Soiled Workroom or Soiled Holding
Small Meeting Room
Large Meeting Room
Private office

## Data Table
Type of Occupancy/Activity | Design sound level range | Project Design Noise Level 1
| (LAeq,t ) | Approx. RC Mark II | dBA
Board and Conference Rooms | 30 to 40 | 35 | 40
Corridors and Lobbies | 45 to 50 | 45 | 50
Executive office | 35 to 40 | 35 | 40
General Office Areas | 40 to 45 | 40 | 45
Meeting room (small) | 40 to 45 | 40 | 45
Open plan office | 40 to 45 | 40 | 45
Public spaces | 40 to 50 | 40 | 45
Quiet rooms | 40 to 45 | 40 | 45
Reception Areas | 40 to 45 | 40 | 45
Rest rooms and break-out spaces | 40 to 45 | 40 | 45
Toilets | 45 to 55 | 45 | 50
Video/audio conference rooms | 30 to 40 | 35 | 40
Type of Occupancy/Activity | Recommended Reverberation Time (s)
Board and Conference Rooms | 0.7
Corridors and Lobbies | 0.7
Executive office | 0.5
General Office Areas | 0.5
Meeting room | 0.6
Open plan office | 0.4
Public spaces | 0.7
Quiet rooms | 0.6
Reception Areas | 0.7
Rest rooms and break-out spaces | 0.5
Toilets | -
Video/audio conference rooms | 0.3
Note 1: Reverberation time should be minimised for noise control.
Room Volume (m3) | RT for Speech (s)
50 | 0.4
100 | 0.5
200 | 0.6
500 | 0.7
1000 | 0.9
2000 | 1
Vocal Effort | Sound Level at 1m
Low | 52
Typical | 60
High | 72
Very High | 78
| Design Vocal Effort within the Source Room | Speech Privacy Level to be Achieved in the Adjoining Space | Privacy rating required
LowNot Sensitive | Low | Not Sensitive | 64 | Low | Not Sensitive | 64
LowMedium Sensitive |  | Medium Sensitive | 69 | Low | Medium Sensitive | 69
LowSensitive |  | Sensitive | 75 | Low | Sensitive | 75
TypicalNot Sensitive | Typical | Not Sensitive | 70 | Typical | Not Sensitive | 70
TypicalMedium Sensitive |  | Medium Sensitive | 75 | Typical | Medium Sensitive | 75
TypicalSensitive |  | Sensitive | 81 | Typical | Sensitive | 81
HighNot Sensitive | High | Not Sensitive | 76 | High | Not Sensitive | 76
HighMedium Sensitive |  | Medium Sensitive | 81 | High | Medium Sensitive | 81
HighSensitive |  | Sensitive | 88 | High | Sensitive | 88
Very HighNot Sensitive | Very High | Not Sensitive | 82 | Very High | Not Sensitive | 82
Very HighMedium Sensitive |  | Medium Sensitive | 88 | Very High | Medium Sensitive | 88
Very HighSensitive |  | Sensitive | 94 | Very High | Sensitive | 94
Note on A24: HP: Note: Small Meeting Room